ASSURED EQUIPMENT GROUNDING CONDUCTOR PROGRAM

PURPOSE

This policy sets out Energy Transport Logistics purpose to outline the appropriate steps in order to verify that equipment is properly grounded. Energy Transport Logistics is committed to providing a safe and healthy work environment by protecting employees from

workplace injury and when reasonably possible to do so.

This procedure specifies minimum requirements for the minimization of static electrical

energy and should be used in conjunction with the site’s Electrical Safety procedures.

Following the steps outlined in this policy will:

- Ensures safety when using temporary power cords (extension cords)

- Reduce risks and prevent injures included but not limited to shock or electrocution

SCOPE

This policy applies to all employees of Energy Transport Logistics, who, regardless of level,

location, or job description, all have a role in creating and maintaining an injury-free workplace.

While the Management of Energy Transport Logistics acknowledges responsibility for

implementing and managing health and safety for the workplace as a whole, employees must

also recognize and accept responsibility for their decisions and actions which can, and will,

affect their own personal safety as well as the personal safety of others.

REFERENCE

HSSE 22.10.01 - BPWE Electrical Safety Procedure

NFPA Standards 70E - Standard for Electrical Safety in the Workplace.

OSHA 29CFR 1910.137 - Electrical Protective Devices

OSHA 29CFR 1910.333 - Selection and Use of Work Practices

OSHA 29CFR 1910 Subpart S - Electrical

KEY RESPONSIBILITIES

Primary responsibility always falls back to the user of any such equipment to verify that

grounding is properly done.

If proper grounding of the equipment in question is beyond the capabilities of the primary

user, then the proper chain of authority shall be used to determine who is qualified to

inspect or install the equipment in question.

PROCEDURES

GENERAL GROUNDING

Personnel shall confirm that the manufacturer’s grounding recommendations are followed when installing or using any electrical equipment or devices.

The grounding conductor shall be the first to be connected and the last to be disconnected.

EQUPIMENT GROUNDING

- The grounding of equipment is primarily for personnel protection and is required for all metallic housings, enclosures, and structures which contain electric conductors.

- Grounding shall be interconnected to the extent that a low potential difference is maintained between nearby metallic objects.

- Equipment grounding applies to motor frames, enclosures for controls, transformer cases, transformer back fences, metallic houses, etc.

The National Electrical Code and National Electric Safety Code shall be referenced to verify equipment grounding requirements are met.

GENERAL- EQUIPMENT INSPECTION, TESTING, AND GFCI USE

- Personnel shall follow all energy isolation requirements before working on any electrical equipment.

- Personnel shall verify that the manufactures grounding recommendations are followed when installing or using any electrical equipment or devices. No one shall bypass or defeat any of these safety devices or systems.

- The grounding conductor shall be the first to be connected and the last to be disconnected if the grounding conductor is separate from the power conductors.

EQUIPMENT INSPECTION, TESTING, AND GFCI USAGE

- Electrical equipment shall be protected by using either Ground Fault Circuit Interrupters (GFCI) or an assured grounding conductor program. Double insulated tools are not required to be grounded or tested.

- All permanent 120-volt single-phase receptacles with a potential to be exposed to water shall have a GFCI type or be protected by a ground fault breaker.

- GFCIs may be of the portable, receptacle, or circuit breaker type and shall be tested periodically (not to exceed three months) to confirm its operability.

- When electrical equipment is used in potentially wet areas and connected to a circuit that does not have a GFCI incorporated, it shall be protected by a portable GFCI.

- All electrical cord sets, portable electric hand tools, and any equipment connected by cord and plug shall be visually inspected prior to use and protected by using either ground fault circuit interrupters or an assured grounding conductor program. (Double insulated tools are not required to be grounded or tested.)

- All 120-volt single phase receptacle outlets that are not part of the permanent wiring of the building or structure and that are in use with the referenced equipment shall have approved ground fault interrupter protection.

Note: Some receptacle outlets that are part of the permanent wiring of the building may not be required to have GFCI protection. However, it is intended that they be used with portable GFCIs and meet the provisions of this section.

ASSURED EQUIPMENT GROUNDING CONDUCTER INSPECTION PROGRAM

Note: The following tests shall be performed on all cord and plug equipment used in a portable fashion or similar equipment that is moved from site to site.

Grounding conductors shall be tested periodically for electrical continuity.

Tests shall be performed by the person responsible for maintaining the equipment as follows:

- Before first use.

- Before equipment is returned to service following any repairs.

- Before equipment is used after an incident that is suspected to have potentially caused damage to equipment, i.e., when a cord is run over.

- At intervals not to exceed three months.

- Each cord set, attachment cap, plug and receptacle of cord sets, and any equipment connected by cord and plug, except those that are fixed and not exposed to damage, shall be visually inspected before each day's use for external defects and for indication of possible internal damage, equipment found damaged or defective may not be used until repaired.

- Tests performed under the Assured grounding conductor-testing program must be documented. Test documentation shall identify each item of equipment tested and indicate the last date it was tested.

- Equipment found to be defective should not be used until repaired.

- All tests other than the visual inspection and periodic testing of the GFCI button shall be documented and kept on file at the applicable field or plant location.

Tests performed under the assured grounding conductor testing program shall be documented and kept on file at the applicable field or plant location. Test documentation shall identify each item of equipment tested and indicate the last date it was tested.

Equipment found to be defective shall be tagged out of service and not used until repaired.

GROUND RODS AND GROUND WIRES

Information on locations and applications requiring ground rods may be found in Engineering Instruction Guidelines Specification 3C200 and Specifications for Engineering Specialties 4A200.

Multiple rods provide a reduction in resistance but may not provide adequate performance.

Ground wires must have sufficient capacity to carry a fault current until short circuit protection opens the circuit.

PERSONAL SAFETY MEASURES

- Hands, shoes, and clothing shall be dry when any energized electrical equipment is handled. Jewelry shall be removed prior to working on energized electrical equipment.

- All protective equipment shall be inspected before each job.

- Do not touch the metal frame of a case if it is ungrounded and you are in contact with the ground or a grounded object.

- Only non-conductive hard hats (ANSI Z87 Class E) are allowed for use where there is a potential for injury from electric shock or burns due to contact with energized parts.

- Only insulated tools or handling equipment shall be used when working near energized equipment if the tools or equipment might come in contact with the parts. The insulating materials of the tools shall be protected against damage and rated for the voltage that may be encountered.

TRAINING

Employees that are required to work on and/or utilize electrical equipment and tools shall be trained on the requirements of this procedure. Training will be documented.

AUDITING

The requirements of this procedure will be audited during each sites annual audit and periodically during monthly site inspections. This procedure shall be audited (and updated as necessary) every three years.